## Sheet1
County Name | School Name | Grade Level | HSFF Category | Project Type | Description/Justification | Total Estimated Project Cost | State Cost Share | Requested State Funding | Funding Approved 9/12/19 | Eligible/ Ineligible/ Deferred | Recommended Eligible Project Cost after reevaluation and prioritzation | Funding Adjustment Recommended 10/10/19 | Funding Recommendation 10/10/19
Anne Arundel | Chesapeake | H | Lead: Piping Replacement | Galvanized Piping | Cold Water Replacement - The 1976 cold water galvanized piping is being replaced with copper piping to stop the corrosion between the galvanized and copper connections. All though numerous repairs have been made to mitigate the leaks it was determined that replacement of the galvanized piping was required. Attached to the application is the full scope and drawings for this project and the March 4, 2019 certified analysis of Chesapeake High School water testing. (Upon reevaluation of the scope of work it was determined that this project did not address an issue with lead above 5 ppb or 20 ppb) | 383000 | 0.5 | 191500 | 191500 | Deferred | 0 | -191500 | 0
Baltimore City | Booker T Washington Building #130 | M/H | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. This building is occupied by 2 schools - Booker T Washington MS and Renaissance Academy. This project is to install vertical packaged HVAC units in all classrooms in the building (approx. 50 classrooms). This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The boilers are 18 years old, and the remainder of the heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. | 2500000 | 0.93 | 2325000 | 2325000 | Approved | 2500000 | 0 | 2325000
Baltimore City | Dickey Hill School #201 | E/M | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. Install vertical packaged HVAC units in all classrooms in the school (approx. 36 classrooms). This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. | 1800000 | 0.93 | 1674000 | 1674000 | Approved | 1800000 | 0 | 1674000
Baltimore City | Edgecombe Circle #62 | E | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. Install vertical packaged HVAC units in all classrooms in the school (approx. 40 classrooms). This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The boilers are 13 years old, and the remainder of the heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. | 2000000 | 0.93 | 1860000 | 1860000 | Approved | 2000000 | 0 | 1860000
Baltimore City | Edgewood School #67 | E | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. Install vertical packaged HVAC units in all classrooms in the school (approx. 26 classrooms). This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The boilers are 10 years old, and the remainder of the heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. | 1300000 | 0.93 | 1209000 | 1209000 | Approved | 1300000 | 0 | 1209000
Baltimore City | Mt. Royal School #66 | E/M | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. Install vertical packaged HVAC units in all classrooms in the school (approx. 42 classrooms). This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The boilers are 18 years old, and the remainder of the heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. | 2100000 | 0.93 | 1953000 | 1953000 | Approved | 2100000 | 0 | 1953000
Baltimore City | Southside Building #181 | H | Immediate Life Safety/Health Environmental Risk | A/C | Vertical Packaged HVAC Unit Installation. This building is occupied by New Era Academy. This project is to install vertical packaged HVAC units in the classrooms used by the school. This includes all of the associated utility service upgrades, electrical requirements to serve the units, and window or louver modifications. This school does not have air conditioning, and the existing heating system is unreliable. The heating system is original to the construction. This project will provide air conditioning and heating to all classrooms. During the last school year, this school dismissed early 4 times due to lack of air conditioning. This school has been impacted by the heating issues in previous years. This project is designed and ready to bid upon funding approval. This school uses bottled water. (IAC staff understands that VPUs if no longer needed can be recycled into future projects) | 2150000 | 0.93 | 1999500 | 0 | Approved | 965250 | 896682 | 896682
Baltimore City | Lakeland PK-8 School #12 | E/M | IAQ: Mold and Mold Potential | Pipe Installation | Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated in 3 classrooms and the media center. In the last year, the school has had 10 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. The existing HVAC system is original to the building construction. This school uses bottled water. | 1030000 | 0.93 | 957900 | 0 | Deferred | 0 | 0 | 0
Baltimore City | Callaway School #251 | E | IAQ: Mold and Mold Potential | Pipe Insulation | Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated in 3 classrooms and the media center. In the last year, the school has had 10 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. The existing HVAC system is original to the building construction. This school uses bottled water. | 945000 | 0.93 | 878850 | 0 | Deferred | 0 | 0 | 0
Baltimore City | Coldstream Park Building #31 | E/M | IAQ: Mold and Mold Potential | Pipe Insulation | This building is occupied by Stadium School #15. The original HVAC pipe insulation has failed, or was not the correct insulation when it was originally installed. This is causing condensation issues throughout the building. The scope of this project will remove and reinstall all existing failed or inadequate pipe insulation, including piping where there is no insulation. The new insulation shall be 1 1/2" thick fiberglass pipe covering with PVC fittings over elbows, 1/2" thick fiberglass duct wrap on supply ducts and Armaflex pipe covering within 12 ft. of fan coil units and unit ventilators. New insulation on chilled water pipes shall have an R value between 8.5 and 10.5 and be rated from 30 degrees to 240 degrees. "Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated in 1 classroom. In the last year, the school has had 14 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. In 2008 this building received a new boiler, chiller, and an electrical upgrade, however the piping, terminal units and remainder of the HVAC system are original to the building construction. This school uses bottled water. | 1000000 | 0.93 | 930000 | 0 | Deferred | 0 | 0 | 0
Baltimore City | Glenmount School #235 | E/M | IAQ: Mold and Mold Potential | Pipe Insulation | The original HVAC pipe insulation has failed, or was not the correct insulation when it was originally installed. This is causing condensation issues throughout the building. The scope of this project will remove and reinstall all existing failed or inadequate pipe insulation, including piping where there is no insulation. The new insulation shall be 1 1/2" thick fiberglass pipe covering with PVC fittings over elbows, 1/2" thick fiberglass duct wrap on supply ducts and Armaflex pipe covering within 12 ft. of fan coil units and unit ventilators. New insulation on chilled water pipes shall have an R value between 8.5 and 10.5 and be rated from 30 degrees to 240 degrees. Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated throughout the entire building. In the last year, the school has had 13 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. This school uses bottled water. | 850000 | 0.93 | 790500 | 0 | Deferred | 0 | 0 | 0
Baltimore City | Liberty School #64 | E | IAQ: Mold and Mold Potential | Pipe Insulation | This building is occupied by Stadium School #15. The original HVAC pipe insulation has failed, or was not the correct insulation when it was originally installed. This is causing condensation issues throughout the building. The scope of this project will remove and reinstall all existing failed or inadequate pipe insulation, including piping where there is no insulation. The new insulation shall be 1 1/2" thick fiberglass pipe covering with PVC fittings over elbows, 1/2" thick fiberglass duct wrap on supply ducts and Armaflex pipe covering within 12 ft. of fan coil units and unit ventilators. New insulation on chilled water pipes shall have an R value between 8.5 and 10.5 and be rated from 30 degrees to 240 degrees. "Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated in 1 classroom. In the last year, the school has had 14 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. In 2008 this building received a new boiler, chiller, and an electrical upgrade, however the piping, terminal units and remainder of the HVAC system are original to the building construction. This school uses bottled water. | 945000 | 0.93 | 878850 | 0 | Deferred | 0 | 0 | 0
Baltimore City | North Bend School #81 | E/M | IAQ: Mold and Mold Potential | Pipe Insulation | The original HVAC pipe insulation has failed, or was not the correct insulation when it was originally installed. This is causing condensation issues throughout the building. The scope of this project will remove and reinstall all existing failed or inadequate pipe insulation, including piping where there is no insulation. The new insulation shall be 1 1/2" thick fiberglass pipe covering with PVC fittings over elbows, 1/2" thick fiberglass duct wrap on supply ducts and Armaflex pipe covering within 12 ft. of fan coil units and unit ventilators. New insulation on chilled water pipes shall have an R value between 8.5 and 10.5 and be rated from 30 degrees to 240 degrees. Condensation occurs when the insulation on the HVAC piping is not adequate. When different temperatures exist between the water in the piping and the surrounding air, condensation occurs. Condensation leads to multiple problems - water damage in the building, mold growth, and pipe rust. Mold is a matter of health and safety, especially in populations with asthma and other breathing conditions. Mold growth sponsors more mold growth until the issue is resolved and the mold is remediated. When the pipes rust, they often leak or burst under the water pressure, causing HVAC systems to not work along with the water damage. This building has exhibited severe condensation issues in the past several years, with the related problems of water leaks, pipes rusting and bursting, and mold. Current corrections have been to spot repair as needed, but the entire piping system needs to be re-insulated to correct the problem. In the last year, mold due to condensation on insulation has been remediated throughout the entire building. In the last year, the school has had 13 work orders submitted for mold or suspected mold on insulation, to repair damaged insulation, and to repair condensation leaks/drips. This school uses bottled water. | 1235000 | 0.93 | 1148550 | 0 | Deferred | 0 | 0 | 0
Baltimore County | Bedford | E | Immediate Life Safety/Health Environmental Risk | A/C | Air conditioning installation, vertical packaged units (VPUs). BCPS has reviewed options for this specific school, and VPUs is the most cost effective, code compliant option. This project will provide air conditioning to at least 19 classrooms and the gymnasium which will be beneficial to our students and staff. This project is intended to be replaced in the future. Providing air conditioning to the unairconditioned spaces is justified as a priority. This school follows the BCPS school closing process if heat index exceed standards and has closed in the past. Please see additional attachments explaining more about Bedford (Cost of gymnasium deducted and IAC staff understands that VPUs if no longer needed can be recycled into future projects) | 3510000 | 0.56 | 1680000 | 1680000 | Approved | 2837000 | -91280 | 1588720
Baltimore County | Campfield Early Learning Center | E | Immediate Life Safety/Health Environmental Risk | A/C | Chiller installation to "chiller ready" school. The school currently is not air conditioned. This project will provide air conditioning to at least 26 classrooms, gymnasium and cafeteria which will be beneficial to our students and staff. This school is currently not air conditioned. This school follows the BCPS school closing process if heat index exceed standards and has closed in the past. Please see additional attachments explaining more about Campfield ELC. (Cost of gymnasium deducted and IAC staff understands that VPUs if no longer needed can be recycled into future projects) | 3295000 | 0.56 | 1540000 | 0 | Approved | 2807000 | 1540000 | 1540000
Baltimore County | Catonsville Center for Alternative Studies | H | Immediate Life Safety/Health Environmental Risk | A/C | Air conditioning installation, vertical packaged units (VPUs). BCPS has reviewed options for this specific school, and VPUs is the most cost effective, code compliant option. This project will provide air conditioning to at least 12 classrooms and the gymnasium which will be beneficial to our students and staff. This school is currently not air conditioned and this project is a priority. This school follows the BCPS school closing process if heat indexes exceed standards and has closed in the past. Please see additional attachments explaining more about Catonsville Alternative School. (Cost of gymnasium deducted) | 1803000 | 0.56 | 842000 | 842000 | Approved | 1223000 | -157120 | 684880
Baltimore County | Dulaney | H | Immediate Life Safety/Health Environmental Risk | A/C | Air conditioning installation, vertical packaged units (VPUs). BCPS has reviewed options for this specific school, and VPUs is the most cost effective, code compliant option. Priority Project - This project will provide air conditioning to at least 50 classrooms, the health suite, the gymnasium, and cafeteria which will be beneficial to our students and staff. An original renovation project was rescinded and providing air conditioning to the unairconditioned spaces is justified. This school follows the BCPS school closing process if heat index exceed standards and has closed in the past. Please see additional attachments explaining more about Dulaney (Cost of gymnasium deducted and IAC staff understands that VPUs if no longer needed can be recycled into future projects) | 7815000 | 0.56 | 3640000 | 3640000 | Approved | 6937000 | 0 | 3640000
Baltimore County | Eastern Technical | H | Immediate Life Safety/Health Environmental Risk | A/C | Installation of Roof Top units with Dx cooling. The original tech wing is not air conditioned, and with the current piping configuration it will be difficult to tie it into the chilled water loop. This project will provide air conditioning to at least 11 classrooms which will be beneficial to our students and staff. This school has a wing that is not currently not air conditioned and this project is a priority. The gymnasium is also not air conditioned. Please see additional attachments explaining more about Eastern Technical High School. (The Cost of gymnasium was deducted from the Total Estimated Project Cost) | 3418000 | 0.56 | 1664000 | 1664000 | Approved | 2328000 | -360320 | 1303680
Baltimore County | Lansdowne | H | Immediate Life Safety/Health Environmental Risk | A/C | Air conditioning installation, vertical packaged units (VPUs). BCPS has reviewed options for this specific school, and VPUs is the most cost effective, code compliant option. This project will provide air conditioning to at approximately 70 classrooms, auditorium, gymnasium, and cafeteria which will be beneficial to our students and staff. An original renovation project was rescinded and providing air conditioning to the unairconditioned spaces is justified. This unairconditioned school follows the BCPS school closing process if heat index exceed standards and has closed in the past. Please see additional attachments explaining more about Lansdowne High. (Cost of gymnasium deducted and IAC staff understands that VPUs if no longer needed can be recycled into future projects) | 8715000 | 0.56 | 4032000 | 4032000 | Approved | 7866000 | 0 | 4032000
Baltimore County | Western School of Technology/Science | H | Immediate Life Safety/Health Environmental Risk | A/C | Installation of Roof Top units with Dx cooling. The original tech wing is not air conditioned, and with the current piping configuration it will be difficult to tie it into the chilled water loop. This project will provide air conditioning to at least 16 classrooms which will be beneficial to our students and staff. This school has a wing that is not currently not air conditioned and this project is a priority. Please see additional attachments explaining more about Western School of Technology/Science. | 2896000 | 0.56 | 1378000 | 1378000 | Approved | 2896000 | 0 | 1378000
Baltimore County | Hampton | E | Non-Immediate Heating | Heating - Boiler Replacement | Boiler replacement. The steam boilers (1998) have been failing. Boiler No. 2 is non-operational and Boiler No. 1 has significant issues. This failure could impact the ability to open up the school in the future. | 535000 | 0.56 | 224000 | 224000 | Approved | 535000 | 0 | 224000
Calvert | Mill Creek | M | Non-Immediate A/C | Gym Rooftop A/C & Heat Pump Unit Replacement a | We have had continual mechanical issues with these Gymnasium Rooftop Packaged Water Source Heat Pump units. Over the past 20 years the units have had compressor replacements , motor replacements , total rewiring of high voltage and welding on the cabinets that came apart . The units have trouble keeping up with heating, cooling, and dehumidification demands. A few years ago, we planned on utilizing QZAB funds to replace the units however the grant program was cancelled that year. Due to their age and the recurring issues , the only solution is to replace both units and continue our detailed preventive maintenance on them . This is also critical because of the wood floors that damage easily from humidity and temperature fluctuations in the gym. A snapshot of work orders from the last 2 years are attached. | 130000 | 0.53 | 68900 | 0 | Deferred | 0 | 0 | 0
Calvert | Mt. Harmony Elementary School | E | Non-Immediate Heating | Heating | The Horizontal Fire Tube Steel Boilers are original to the building. When replacing the refractory brick inside the burner chamber for both units, it was discovered that there was significant rusting inside, to the point where layers of steel on the inside of the boilers is flaking off into the burner chamber itself. Investigation found that the boiler changeover valves were leaking, and because this building has a dual temperature piping system for its central plant, during the cooling season, chilled water had been continually migrating into the boilers, causing condensation, which ultimately turned into rust. We propose replacing both 100 HP boilers, changeover valves and associated piping. This would ensure that we are resolving all critical issues related to the heating plant. Pictures of the existing condition inside the burner chambers are attached. | 117000 | 0.53 | 62010 | 62010 | Approved | 117000 | 0 | 62010
Carroll | Westminster | H | Windows/Structural/ Other Structural | Wall Reconstruction | This project involves the reconstruction of the top band of brick as a cavity wall with through wall flashing and repair/replacement of steel lintels. During the 2018-19 school year, the school experienced water infiltration in various 3rd floor classrooms. As a result, CCPS hired a consultant to determine the cause of this water infiltration. The consultant concluded that the root cause was water infiltration through deteriorated mortar joints. Additionally, they found that the flashings intended to expel water to the exterior were not correctly placed. The flashing terminates 2 inches from the exterior face, which allows water capture by the flashing to migrate back into the wall. As a result, the water within the wall keeps the masonry saturated. Freeze-thaw cycles of the saturated brick and mortar allow for accelerated deterioration. Pieces of mortar have been falling from this area, and CCPS has placed temporary canopies by the front door to prevent students from being hit by falling debris. It was our intent to apply for this project in the spring, because these repairs needed to begin this summer. Due to the delay in issuing the application procedures, Carroll made a decision to move ahead with awarded the contract prior to applying for the project. These repairs needed to be done as summer work, and we could not wait another summer. The Board awarded the contract in June and repairs are underway. | 908750 | 0.59 | 536163 | 0 | Deferred | 0 | 0 | 0
Cecil | Bay View | E | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Bohemia Manor | M/H | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Cecil Manor | E | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Cecil School of Technology | H | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Charlestown | E | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Cherry Hill | M | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Elkton | M | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Elkton | H | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Kenmore | E | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | North East | E | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | North East | M | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | North East | H | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Perryville | M | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Perryville | H | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Rising Sun | M | Immediate Life Safety/Health Environmental Risk | Lead | This funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Thomas Estates | E | Immediate Life Safety/Health Environmental Risk | Lead | Attached please find the spreadsheets indicating the specific sites where this funding request would be used to assist with costs of implementing remedial measures to address the presence of lead in drinking water outlets. These remedial measures would include repairing/replacing water fixtures and plumbing components that have been identified through testing to have elevated levels of lead above 20ppb. | 4375 | 0.66 | 2887.5 | 2887.5 | Approved | 4375 | 0 | 2887.5
Cecil | Rising Sun HS - Gymnasium HVAC upgrades |  | Non-Immediate A/C | HVAC - Gym | The existing gymnasium does not currently have Air Conditioning. The school has experienced dangerous temp. during sporting and school related events resulting in unsafe health conditions. We desire to replace the existing gymnasium H&V RTU with a HVAC RTU with hydronic heating coil. Work to include demo the existing H&V unit. Isolate the heating water supply & return pipes. Lockout/ Tagout the power supply to the existing unit and disconnect the associated ductwork. Remove the existing unit and install the new unit with the use of a crane. Upgrade the existing power supply from the main electrical distribution room to the unit on the roof of the gymnasium to accommodate for adding A/C to the new unit. New conduit and wire will have to be ran/ pulled, a new switchgear bucket and unit disconnect will be furnished and installed. Connect the heating supply and return piping to the new HVAC RTU. Connect the new unit to a newly supplied and installed Duct-sock in the gymnasium. (Supply and return). If a new curb adapter is required, we will supply this. Furnish and Install new PVC schedule 40 pipe and fittings for the condensate drain line. | 176000 | 0.66 | 116160 | 0 | Deferred | 0 | 0 | 0
Cecil | Bohemia Manor | M | Non-Immediate A/C | HVAC Relocatable CR: Mold Remediation | Replace/upgrade existing HVAC system in three (3) relocatable classrooms to reduce the current CO2 output and current existence of mold and moisture to include new Carrier 3 Ton Heat pump with backup Electric Heat, all new ductwork and insulation, new JCI - gateway + CO2 sensor, new JCI - TEC DDC thermostat, new JCI - OA damper actuator, new JCI - FEC controller, new DDC wiring, and new power wiring. | 97500 | 0.66 | 64350 | 64350 | Approved | 97500 | 0 | 64350
Cecil | Kenmore | E | Non-Immediate A/C | HVAC Replacement Relocatable CR: Mold Remediation | Replace/upgrade existing HVAC system in three (3) relocatable classrooms to reduce the current CO2 output and current existence of mold and moisture to include new Carrier 3 Ton Heat pump with backup Electric Heat, all new ductwork and insulation, new JCI - gateway + CO2 sensor, new JCI - TEC DDC thermostat, new JCI - OA damper actuator, new JCI - FEC controller, new DDC wiring, and new power wiring. | 97500 | 0.66 | 64350 | 64350 | Approved | 97500 | 0 | 64350
Cecil | North East | H | Non-Immediate A/C | HVAC Upgrade - Gym | The existing gymnasium does not currently have Air Conditioning. The school has experienced dangerous temp. during sporting and school related events resulting in unsafe health conditions. We desire to replace the existing gymnasium H&V RTU with a HVAC RTU with hydronic heating coil. Work it include demo of existing H&V unit. Isolating the heating water supply & return pipes. Lockout/ Tag out the power supply to the existing unit and disconnect the associated ductwork. Remove the existing unit and install the new unit with the use of a crane. Upgrade the existing power supply from the main electrical distribution room to the unit on the roof of the gymnasium to accommodate for adding A/C to the new unit. New wire will have to be pulled, a new switchgear bucket and unit disconnect will be furnished and installed. Connect the heating supply and return piping to the new HVAC RTU. Connect the new unit to the existing ductwork in the gymnasium. (Supply and return). If a new curb adapter is required, we will supply this. Furnish and Install new PVC schedule 40 pipe and fittings for the condensate drain line. | 137500 | 0.66 | 90750 | 0 | Deferred | 0 | 0 | 0
Harford | CEO |  | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Harford | Deerfield | E | Lead: Drinking Water Outlets | Lead | Filtered water bottle filling stations use high-performance filters that remove common contaminants such as chlorine, particulates, and lead. This project would provide-high performance filtered bottle filling stations for the remaining Harford County Public Schools that do not currently have them within the school building. This will provide students access to safe, clean drinking water containing no harmful byproducts and a more appealing alternative to other beverage choices. Additionally, this will prevent potential elevated lead contaminants in drinking water in the future. (This school did not test above 5 ppb) | 9000 | 0.63 | 5670 | 0 | Deferred | 0 | 0 | 0
Harford | Dublin | E | Lead: Drinking Water Outlets | Lead | Filtered water bottle filling stations use high-performance filters that remove common contaminants such as chlorine, particulates, and lead. This project would provide-high performance filtered bottle filling stations for the remaining Harford County Public Schools that do not currently have them within the school building. This will provide students access to safe, clean drinking water containing no harmful byproducts and a more appealing alternative to other beverage choices. Additionally, this will prevent potential elevated lead contaminants in drinking water in the future. (This school did not test above 5 ppb) | 0 |  | 0 | 0 | Deferred | 0 | 0 | 0
Harford | Edgewood | M | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Harford | Forest Lakes | E | Lead: Drinking Water Outlets | Lead | Filtered water bottle filling stations use high-performance filters that remove common contaminants such as chlorine, particulates, and lead. This project would provide-high performance filtered bottle filling stations for the remaining Harford County Public Schools that do not currently have them within the school building. This will provide students access to safe, clean drinking water containing no harmful byproducts and a more appealing alternative to other beverage choices. Additionally, this will prevent potential elevated lead contaminants in drinking water in the future. (This school did not test above 5 ppb) | 0 |  | 0 | 0 | Deferred | 0 | 0 | 0
Harford | Homestead | E | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Harford | Magnolia | M | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Harford | Riverside | E | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Harford | Wakefield | E | Immediate Life Safety/Health Environmental Risk | Lead | This project would replace water fountains with filtered water bottle filling stations at schools with drinking fountains with lead testing results greater than 20 parts per billion (ppb). The filter water bottle filling station contain high-performance filters that remove common contaminants including lead. This is the most effective, efficient, and affordable method to address the issue and provide students with safe drinking water. | 3000 | 0.63 | 1890 | 1890 | Approved | 3000 | 0 | 1890
Montgomery | Lead in Water Fixture Replacement |  | Lead: Drinking Water Outlets | Water Fixture Replacement | The Montgomery County Council passed legislation in 2019 that lowered the lead in water action level from 20 parts per billion (ppb) to 5 ppb. MCPS staff removed 272 bubblers and 10 coolers from service that tested greater than 5 ppb in all MCPS schools and facilities. MCPS is developing a replacement plan for these fixtures, prioritizing the classrooms serving younger children. (The cost for labor has been removed from the Total Estimated Project Cost). | 182400 | 0.5 | 91200 | 0 | Approved | 136700 | 68350 | 68350
Montgomery | Sargent Shriver | E | Non-Immediate Heating | Heating | Replacement of two boilers. • 1 has a cracked secondary heat exchanger (condensing side) and is leaking water. • 2nd boiler - secondary heat exchanger is completely clogged with rust. It is a steel heat exchanger and cannot be cleaned and made operational. • Both boilers must be replaced in order to properly synchronize the control circuits without additional significant costs. | 128000 | 0.5 | 64000 | 64000 | Approved | 128000 | 0 | 64000
Montgomery | Belmont | E | Non-Immediate A/C | HVAC replacement | Emergency replacement of air cooled chiller. • 2004 Trane air cooled, expected service life was 20 years, it is only 15 years old. • Chiller is full of water and repair costs far exceed replacement. • Circuit A is operational, but unable to carry the full load once school is back in session. • Board approved contractor indicates that a stock chiller is scheduled to come off the assembly line in early August and could be installed and running prior to school opening. | 165000 | 0.5 | 82500 | 82500 | Approved | 165000 | 0 | 82500
Montgomery | Emory Grove Center | E | Non-Immediate A/C | HVAC replacement | Emergency replacement of two air cooled 50 ton chillers. These units are inoperable and must be replaced. We have rented temporary units for the summer occupied classrooms, until the replacement units can be installed • 1992 Carrier air cooled, expected service life was 20 years, they are 27 years old. • The controls are obsolete (unavailable) and malfunctioning in addition to being non upgradeable. Carrier Mid- Atlantic advises there are no replacement control available for these series chillers. • 2 chillers with 2 circuits consisting of 2 compressors each. We have multiple leaks in the condenser coils, faulty Thermostatic expansion valve and possibly other sealed system issues that cannot be diagnosed without the chillers running. • One chiller is capable of running the facility, while the other chiller is for redundancy. • Each machine holds around 200lbs of R-22. This refrigerant is scheduled for full phase out by 2020. • The full cost of repairs on both chiller exceed the price of replacement. The lead time on the repairs will exceed 4-6 weeks. | 185000 | 0.5 | 92500 | 92500 | Approved | 185000 | 0 | 92500
Montgomery | Georgian Forest | E | Non-Immediate A/C | HVAC replacement | Emergency replacement of air cooled chiller. • 1995 Carrier air cooled, expected service life was 20 years, it is now 24 years old. • The controls are obsolete (unavailable) and malfunctioning in addition to being non upgradeable. Carrier Mid- Atlantic advises there are no replacements for this series via telephone for GN series chillers. • 2 circuits consisting of 2 compressors each. 1 circuit has a grounded compressor and there is a leak on the condenser side which is the potential cause for burnout. • Only 1 circuit capable of running, not capable of sustaining load and no redundancy in the building. • Machine holds a little over 200 lbs of R-22 and is leaking refrigerant (environmental hazard). • Emergency replacement in order to have operational by school opening. | 121000 | 0.5 | 60500 | 60500 | Approved | 121000 | 0 | 60500
Montgomery | Lincoln Center | E | Non-Immediate A/C | HVAC replacement | Emergency replacement of two condensing units and two air handler units (part of HVAC system). • Current system is inadequate and unable to properly cool the building. • Area directly impacted supports media processing and text books for schools. Project was determined to be ineligible because no students occupy this facility. | 180000 | 0.5 | 73500 | 0 | Ineligible | 0 | 0 | 0
Montgomery | Silver Spring International & Sligo Creek | E/M | IAQ: Mold and Mold Potential | School masonry repairs and waterproofing | Repair and waterproof masonry walls that are leaking over an extended period of time and causing interior moisture intrusion and the potential for mold. | 250000 | 0.5 | 125000 | 0 | Deferred | 0 | 0 | 0
Montgomery | Poolesville | H | IAQ: Mold and Mold Potential | School masonry repairs and waterproofing | Repair and waterproof masonry walls that are leaking over an extended period of time and causing interior moisture intrusion and the potential for mold. | 147000 | 0.5 | 73500 | 0 | Deferred | 0 | 0 | 0
Montgomery | Lake Seneca | E | IAQ: Mold and Mold Potential | School masonry repairs and waterproofing | Repair and waterproof masonry walls that are leaking over an extended period of time and causing interior moisture intrusion and the potential for mold. | 179000 | 0.5 | 89500 | 0 | Deferred | 0 | 0 | 0
Montgomery | Spark M. Matsunaga | E | IAQ: Mold and Mold Potential | School masonry repairs and waterproofing | Repair and waterproof masonry walls that are leaking over an extended period of time and causing interior moisture intrusion and the potential for mold. | 108000 | 0.5 | 54000 | 0 | Deferred | 0 | 0 | 0
Montgomery | Col. Zadock Magruder | H | IAQ: Mold and Mold Potential | School masonry repairs and waterproofing | Windows are old (49 years) and have the potential for allowing interior moisture intrusion and the potential for mold. In addition, they are not well insulated and result in difficult temperature regulation for the students. | 211000 | 0.5 | 105500 | 0 | Deferred | 0 | 0 | 0
Prince George's | H. Winship Wheatley Early Education Childhood Center Upper and Lower Campus Renovation | E | Non-Immediate HVAC System | HVAC Replacement with Gym included | The scope of work is to replace the upper campus boiler, piping, downstream units in the upper campus, and provide new dedicated outside air units to provide preconditioned outside air to the entire facility. Scope of work also includes full controls upgrade. The existing sprinkler system will need to be extended to the rest of the facility or replaced in its entirety. A full fire alarm upgrade will be required as well. Affected areas in scope would include full ceiling replacement throughout with LED lighting upgrade. (Cost of sprinkler and ceiling/lighting deducted and the cost of the gymnasium was included because this facility services regional special education) | 8094126 | 0.7 | 5665888 | 5665888 | Approved | 7106483 | -691350 | 4974538
St. Mary's | Town Creek | E | Windows/IAQ: Asbestos | Window Replacement (Asbestos) | Remove and dispose of asbestos window glazing on the interior and exterior of 81 windows and re-glaze the windows. The windows are original to the building. The asbestos window glazing is very brittle and becomes loose causing emergency situations where it has to be removed due to the accessibility of the product to students. The cracked and missing glazing allows for water infiltration and the potential for mold. Any release of fibers requires immediate action to contain the release, the room is vacated, and a plan for remediation is developed and undertaken based on recommendations from a certified vendor. We were fortunate that small amounts can be remediated at a time while avoiding any loss of school. However, if large amounts become loose, we must have an outside vendor complete the work and the risk remains that students/staff may need to be removed from the classroom causing a disruption to the program. To avoid disruption to the school environment due to continued failure, we are seeking funds to remediate the interior and exterior asbestos material. Staff at the school monitors this glazing on a regular basis. The replacement of the windows has been deferred several years due to funding constraints. This work will have to be coordinated with the school if the approval does not allow the work to be done prior to school starting. Given the timeline for review and approval, we anticipate this work will be done during holiday breaks. The inspection of the facilities does not include the exterior of the window, however, we have completed inspections and verifications on an as needed basis and determined that this era of window does contain ACM. We are currently in the process of having an updated inspection scheduled in anticipation of approval of this project which will be completed with local funds. Of importance, this glazing must be abated prior to application of the ballistic resistant laminate. It is imperative that we remove the ACM for life safety and to secure our facilities as part of our safety initiative. We currently have a funding stream available as of July 2019 to cover the local match. (There was not enough information available to make the determination that this project request would resolve a threat to the immediate life, safety and environmental health of the occupants of the building. Testing results for this school was unavilable) | 340848 | 0.58 | 197692 | 197692 | Deferred | 0 | -197692 | 0
St. Mary's | Ridge | E | Windows/IAQ: Asbestos | Window Replacement (Asbestos) | Remove and dispose of asbestos window glazing on the interior and exterior of 45 windows and re-glaze the windows. The windows are original to the building. The asbestos window glazing is very brittle and becomes loose causing emergency situations where it has to be removed due to the accessibility of the product to students. The cracked and missing glazing allows for water infiltration and the potential for mold. Any release of fibers requires immediate action to contain the release, the room is vacated, and a plan for remediation is developed and undertaken based on recommendations from a certified vendor. We were fortunate that small amounts can be remediated at a time while avoiding any loss of school. However, if large amounts become loose, we must have an outside vendor complete the work and the risk remains that students/staff may need to be removed from the classroom causing a disruption to the program. To avoid disruption to the school environment due to continued failure, we are seeking funds to remediate the interior and exterior asbestos material. Staff at the school monitors this glazing on a regular basis. The replacement of the windows has been deferred several years due to funding constraints. This work will have to be coordinated with the school if the approval does not allow the work to be done prior to school starting. Given the timeline for review and approval, we anticipate this work will be done during holiday breaks. The inspection of the facilities does not include the exterior of the window, however, we have completed inspections and verifications on an as needed basis and determined that this era of window does contain ACM. We are currently in the process of having an updated inspection scheduled in anticipation of approval of this project which will be completed with local funds. Of importance, this glazing must be abated prior to application of the ballistic resistant laminate. It is imperative that we remove the ACM for life safety and to secure our facilities as part of our safety initiative. We currently have a funding stream available as of July 2019 to cover the local match. (There was not enough information available to make the determination that this project request would resolve a threat to the immediate life, safety and environmental health of the occupants of the building. Testing results for this school was unavilable) | 189360 | 0.58 | 109829 | 88189 | Deferred | 0 | -88189 | 0
St. Mary's | Mechanicsville | E | Windows/IAQ: Asbestos | Window Replacement (Asbestos) | Remove and dispose of asbestos window glazing on the interior and exterior of 126 windows and re-glaze the windows. The windows are original to the building. The asbestos window glazing is very brittle and becomes loose causing emergency situations where it has to be removed due to the accessibility of the product to students. The cracked and missing glazing allows for water infiltration and the potential for mold. Any release of fibers requires immediate action to contain the release, the room is vacated, and a plan for remediation is developed and undertaken based on recommendations from a certified vendor. We were fortunate that small amounts can be remediated at a time while avoiding any loss of school. However, if large amounts become loose, we must have an outside vendor complete the work and the risk remains that students/staff may need to be removed from the classroom causing a disruption to the program. To avoid disruption to the school environment due to continued failure, we are seeking funds to remediate the interior and exterior asbestos material. Staff at the school monitors this glazing on a regular basis. The replacement of the windows has been deferred several years due to funding constraints. This work will have to be coordinated with the school if the approval does not allow the work to be done prior to school starting. Given the timeline for review and approval, we anticipate this work will be done during holiday breaks. The inspection of the facilities does not include the exterior of the window, however, we have completed inspections and verifications on an as needed basis and determined that this era of window does contain ACM. We are currently in the process of having an updated inspection scheduled in anticipation of approval of this project which will be completed with local funds. Of importance, this glazing must be abated prior to application of the ballistic resistant laminate. It is imperative that we remove the ACM for life safety and to secure our facilities as part of our safety initiative. We currently have a funding stream available as of July 2019 to cover the local match. (There was not enough information available to make the determination that this project request would resolve a threat to the immediate life, safety and environmental health of the occupants of the building. Samples of interior window caulking tested negative for asbestos content). | 490758 | 0.58 | 284639 | 284639 | Deferred | 0 | -284639 | 0
St. Mary's | White Marsh | E | Windows/IAQ: Asbestos | Window Replacement (Asbestos) | Remove and dispose of asbestos window glazing on the interior and exterior of 63 windows and re-glaze the windows. The windows are original to the building. The asbestos window glazing is very brittle and becomes loose causing emergency situations where it has to be removed due to the accessibility of the product to students. The cracked and missing glazing allows for water infiltration and the potential for mold. Any release of fibers requires immediate action to contain the release, the room is vacated, and a plan for remediation is developed and undertaken based on recommendations from a certified vendor. We were fortunate that small amounts can be remediated at a time while avoiding any loss of school. However, if large amounts become loose, we must have an outside vendor complete the work and the risk remains that students/staff may need to be removed from the classroom causing a disruption to the program. To avoid disruption to the school environment due to continued failure, we are seeking funds to remediate the interior and exterior asbestos material. Staff at the school monitors this glazing on a regular basis. The replacement of the windows has been deferred several years due to funding constraints. This work will have to be coordinated with the school if the approval does not allow the work to be done prior to school starting. Given the timeline for review and approval, we anticipate this work will be done during holiday breaks. The inspection of the facilities does not include the exterior of the window, however, we have completed inspections and verifications on an as needed basis and determined that this era of window does contain ACM. We are currently in the process of having an updated inspection scheduled in anticipation of approval of this project which will be completed with local funds. Of importance, this glazing must be abated prior to application of the ballistic resistant laminate. It is imperative that we remove the ACM for life safety and to secure our facilities as part of our safety initiative. We currently have a funding stream available as of July 2019 to cover the local match. (There was not enough information available to make the determination that this project request would resolve a threat to the immediate life, safety and environmental health of the occupants of the building. Testing results for this school was unavilable) | 265104 | 0.58 | 157760 | 0 | Deferred | 0 | 0 | 0
Washington | Williamsport | H | Lead: Piping Replacement | Galvanized Piping | Williamsport High School Domestic Water Line Replacement. This project is intended to replace the existing galvanized domestic waterlines at Williamsport High School that are beginning to scale and erode. The domestic water lines are original to the school (built 1970). (Upon reevaluation of the scope of work for this project, it was determined that this project did not address lead levels above 5 ppb). This erosion of the interior of the galvanized pipe causes the water to turn a brown color, and occasionally discharge sediment after sitting over a weekend. The galvanized domestic water lines at Williamsport High School consist of the following: Approximately 50 feet of 8 inch galvanized reduced to 6 Inch incoming building main. Approximately 100 feet of 4 inch galvanized. Approximately 500 feet of 3 inch galvanized. WCPS recently completed similar replacement projects at two (2) other schools that had the same type of domestic water line construction (galvanized pipe). Photos showing what the interior of these lines look like (as the galvanized material has eroded) from these two projects is included. These lines carried the drinking water for the school facility prior to replacement. Additionally, there are a couple of locations at Williamsport High School where the identified galvanized lines run above hard ceilings, and asbestos insulation is expected to be on the lines (areas that were/are accessible, had the asbestos insulation previously removed). There are also a couple of locations in the boiler room where some asbestos insulation (elbows) remains on the existing galvanized domestic water lines. | 150000 | 0.71 | 106500 | 106500 | Deferred | 0 | -106500 | 0
Washington | Boonsboro | H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #5. Replace 22 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended for drinking outlets only. There was no evidence that the sink fixtures were used for prepare food). | 15000 | 0.71 | 10650 | 10650 | Deferred | 0 | -10650 | 0
Washington | Boonsboro | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #6. Replace 20 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 14000 | 0.71 | 9940 | 9940 | Deferred | 0 | -9940 | 0
Washington | Boonsboro Middle School | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #4. Replace 2 drinking fountains, and 18 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 17000 | 0.71 | 12070 | 12070 | Approved | 3944 | -9270 | 2800
Washington | Cascade | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #2. Replace 3 drinking fountains, and 16 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 18000 | 0.71 | 12780 | 12780 | Approved | 5915 | -8580 | 4200
Washington | Claud Kitchens Outdoor School |  | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #9. Replace 1 drinking fountain, and 11 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 10000 | 0.71 | 7100 | 7100 | Approved | 1971 | -5700 | 1400
Washington | Clear Spring | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #10. Replace 12 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 9000 | 0.71 | 6390 | 6390 | Deferred | 0 | -6390 | 0
Washington | Clear Spring High School | H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #3. Replace 1 drinking fountain, and 22 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 17000 | 0.71 | 12070 | 12070 | Approved | 1971 | -10670 | 1400
Washington | E.R. Hicks | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #18. Replace 6 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 5000 | 0.71 | 3550 | 0 | Deferred | 0 | 0 | 0
Washington | Hancock | M/H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #1. Replace 1 drinking fountain, and 29 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 22000 | 0.71 | 15620 | 15620 | Approved | 1971 | -14220 | 1400
Washington | Hancock | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #8. Replace 18 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility.(Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 13000 | 0.71 | 9230 | 9230 | Deferred | 0 | -9230 | 0
Washington | Marshall Street School | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #19. Replace 6 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 5000 | 0.71 | 3550 | 0 | Deferred | 0 | 0 | 0
Washington | North Hagerstown | H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #17. Replace 6 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 5000 | 0.71 | 3550 | 0 | Deferred | 0 | 0 | 0
Washington | Northern | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #13. Replace 10 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 8000 | 0.71 | 5680 | 5680 | Deferred | 0 | -5680 | 0
Washington | Paramount | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #20. Replace 6 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 5000 | 0.71 | 3550 | 0 | Deferred | 0 | 0 | 0
Washington | Pleasant Valley | E | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #12. Replace 11 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 8000 | 0.71 | 5680 | 5680 | Deferred | 0 | -5680 | 0
Washington | Smithsburg | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #15. Replace 8 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 7000 | 0.71 | 4970 | 0 | Deferred | 0 | 0 | 0
Washington | Springfield | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #7. Replace 19 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 13000 | 0.71 | 9230 | 9230 | Deferred | 0 | -9230 | 0
Washington | Washington County | H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #14. Replace 1 drinking fountain, and 7 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 8000 | 0.71 | 5680 | 5680 | Approved | 1971 | -4280 | 1400
Washington | Western Heights | M | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #16. Replace 7 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 5000 | 0.71 | 3550 | 0 | Deferred | 0 | 0 | 0
Washington | Williamsport | H | Lead: Drinking Water Outlets | Water Fixture Replacement | Water Fixture Replacement Project #11. Replace 2 drinking fountain, and 4 sink fixtures that all tested between 5 ppb and 20 ppb for lead. See attached sheet for additional information. Drinking Fountains are estimated (based on recent WCPS costs to replace using internal forces) to cost $1,400 each in material. Sink Fixtures are estimated (based on recent WCPS costs to replace using internal forces) to cost $150 each. Both of these material estimates include connection lines from sink/faucet to ball valve on branch line Washington County Public Schools intends to award the contract for the above services (if approved for HSFF funding) along with all other Water Fixture Replacement Projects (if approved for HSFF funding) to one (1) Contractor. The Bid form will be set up to identify pricing for each school facility. (Funding is being recommended to drinking fountains projects only. There was no evidence that the sink fixtures were used for prepare food). | 8000 | 0.71 | 5680 | 5680 | Approved | 3943 | -2880 | 2800
Wicomico | Glen Avenue | E | Non-Immediate A/C | A/C | Air Conditioning - There is currently NO air conditioning in Glen Avenue’s Gymnasium or Cafeteria. Glen Avenue’s classrooms are served by window air conditioners that are several years old. This project would be to provide a VRF system without heat recovery, with a roof mounted DOAS unit, condensate, ductwork and power in the Cafeteria and a split system unit (hydronic heat and air cooled condensing unit), new relief louvers, DuctSox, condensate, and power in the Gymnasium. When classroom AC units fail, Administration relocates students to larger spaces such as Gyms or Cafeterias on a temporary basis. Without AC in the Gym or Cafeteria at this school, if there are a significant # of window AC failures in the classrooms, the school would be at risk of closure. Adding AC in the Gym and Cafeteria would assist in the short and long term while we further investigate resolution of the existing classroom window AC units. This is not part of the 2008 RTU project.(Cost of gymnasium deducted - funding applied to the classrooms that have failing air conditioning) | 318600 | 0.97 | 309042 | 309042 | Approved | 87629 | -224042 | 85000
Wicomico | Salisbury | M | Non-Immediate A/C | A/C Gym | Air Conditioning - There is currently NO air conditioning in Salisbury Middle’s Gymnasium. We previously applied for ACI FY14 funds for this project and it was determined ineligible due to age (by 1 year). These areas were excluded from the 1999 completed renovations of Salisbury Middle. This project would provide cooling equipment to existing Trane AHU’s and new condensing units. Existing ductwork to remain. This Gymnasium serves many different school and community programs (after school basketball, parks & recreation programs) as well as regional programs (DI, Special Olympics, etc.) because of its centralized location of the surrounding Eastern Shore Counties. These are the last of the secondary level gymnasiums that don't have air conditioning. | 419500 | 0.97 | 406915 | 0 | Deferred | 0 | 0 | 0
Wicomico | Delmar | E | Windows/Structural/ Other Structural | Window Replacement | Window Replacement - The scope of work includes the removal and replacement of all existing exterior windows and doors at Delmar Elementary School. The existing windows and doors are original to the building. The windows are single pane glazed units and in most locations are supported on existing through-wall mechanical units that are being replaced. The window and door assemblies are leaking due to age of the materials and are in need of replacement with energy efficient units that are properly supported. The exterior window and door units have been maintained throughout the life of the building with new sealants applied and repairs made when needed, however the useful life of these units has been exceeded. The replacement of the exterior doors and windows with new energy efficient units with new sealants and attached to the building structure in lieu of resting on the mechanical units will correct the issue. Delmar ES is one of the highest ranked schools on Wicomico's Facility Needs Index for Systemic. This is not included in the scope of work currently underway with the Limited Renovation. | 690000 | 0.97 | 669300 | 0 | Deferred | 0 | 0 | 0